## CaseInitLoads
Case1 | No Q limits enforced | [5 empty] | Case2 | Q limits enforced
| Voltage Magnitude | Voltage Angle
Bus |  |  | P_Gen | Q_Gen | P_Load | Q_Load
1 | 1.001 | 0.2 | - | - | - | - | Newton's method power flow converged in 3 iterations.
2 | 0.978 | 0.339 | - | - | 1.19 | 0.61 | All 2 remaining gens exceed their Q limits : INFEASIBLE PROBLEM
3 | 1.001 | 0.263 | - | - | - | -
4 | 1 | 0.002 | - | - | - | - | >>>>> Did NOT converge (0.00 seconds) <<<<<
5 | 0.996 | 1.902 | - | - | - | -
6 | 0.997 | 0.088 | - | - | - | - | When voltages changed to one obtained from opf, there is solution
7 | 1 | 0.002 | - | - | - | -
8 | 0.998 | 1.929 | - | - | - | - |  | Voltage Magnitude | Voltage Angle
9 | 0.996 | 1.91 | - | - | - | - | Bus |  |  | P_Gen | Q_Gen | P_Load | Q_Load
10 | 0.995 | 1.926 | - | - | - | - | 1 | 1.001 | 0.149 | - | - | - | -
11 | 0.992 | -0.047 | - | - | 0.22 | 0.01 | 2 | 0.988 | 0.175 | - | - | 1.19 | 0.61
12 | 0.994 | -0.051 | - | - | 0.14 | 0.09 | 3 | 1.002 | 0.212 | - | - | - | -
13 | 0.993 | -0.077 | - | - | 0.16 | 0.09 | 4 | 1 | 0.002 | - | - | - | -
14 | 0.986 | -0.292 | - | - | 0.71 | 0.64 | 5 | 0.996 | 1.85 | - | - | - | -
15 | 0.978 | -1.624 | - | - | 2.5 | 1.2 | 6 | 0.997 | 0.087 | - | - | - | -
16 | 0.996 | 1.845 | - | - | 0.09 | 0.04 | 7 | 1 | 0.001 | - | - | - | -
17 | 0.995 | 1.683 | - | - | 0.14 | 0.01 | 8 | 0.998 | 1.877 | - | - | - | -
18 | 0.986 | 1.359 | - | - | 0.28 | 0.1 | 9 | 0.996 | 1.858 | - | - | - | -
19 | 0.96 | 0.512 | - | - | 0.78 | 0.42 | 10 | 0.995 | 1.874 | - | - | - | -
20 | 0.995 | 1.926 | - | - | - | - | 11 | 0.992 | -0.098 | - | - | 0.22 | 0.01
21 | 1.007 | 4.734 | - | - | -3.5 | -0.01 | 12 | 0.994 | -0.052 | - | - | 0.14 | 0.09
22 | 1 | 0.000* | 1.91 | 4.74 | - | - | 13 | 0.993 | -0.078 | - | - | 0.16 | 0.09
23 | 1 | 3.512 | 1 | -1.08 | - | - | 14 | 0.986 | -0.293 | - | - | 0.71 | 0.64
|  | Total: | 2.91 | 3.67 | 2.7 | 3.21 | 15 | 0.978 | -1.624 | - | - | 2.5 | 1.2
[7 empty] | 16 | 0.997 | 1.793 | - | - | 0.09 | 0.04
[7 empty] | 17 | 0.995 | 1.631 | - | - | 0.14 | 0.01
[7 empty] | 18 | 0.986 | 1.307 | - | - | 0.28 | 0.1
[7 empty] | 19 | 0.961 | 0.461 | - | - | 0.78 | 0.42
[7 empty] | 20 | 0.995 | 1.874 | - | - | - | -
[7 empty] | 21 | 1.008 | 4.681 | - | - | -3.5 | -0.01
[7 empty] | 22 | 1 | 0.000* | 1.86 | 3.98 | - | -
[7 empty] | 23 | 1.02 | 1.718 | 1 | -0.36 | - | -
[9 empty] | Total: | 2.86 | 3.62 | 2.7 | 3.21

## Caset=7000
Case1 | No Q limits enforced | [5 empty] | Case2 | Q limits enforced
| Voltage Magnitude | Voltage Angle | [5 empty] | Voltage Magnitude | Voltage Angle
Bus |  |  | P_Gen | Q_Gen | P_Load | Q_Load | Bus |  |  | P_Gen | Q_Gen | P_Load | Q_Load
1 | 0.997 | 0.138 | - | - | - | - | 1 | 0.978 | 0.087 | - | - | - | -
2 | 0.976 | 0.259 | - | - | 1.19 | 0.61 | 2 | 0.966 | 0.05 | - | - | 1.19 | 0.61
3 | 0.996 | 0.116 | - | - | - | - | 3 | 0.977 | 0.064 | - | - | - | -
4 | 1 | -0.004 | - | - | - | - | 4 | 0.98 | -0.005 | - | - | - | -
5 | 0.984 | -0.589 | - | - | - | - | 5 | 0.964 | -0.671 | - | - | - | -
6 | 0.996 | 0.104 | - | - | - | - | 6 | 0.976 | 0.108 | - | - | - | -
7 | 1 | -0.004 | - | - | - | - | 7 | 0.98 | -0.004 | - | - | - | -
8 | 0.984 | -0.584 | - | - | - | - | 8 | 0.965 | -0.665 | - | - | - | -
9 | 0.983 | -0.581 | - | - | - | - | 9 | 0.964 | -0.662 | - | - | - | -
10 | 0.982 | -0.565 | - | - | - | - | 10 | 0.963 | -0.645 | - | - | - | -
11 | 0.985 | -0.247 | - | - | 0.26 | 0.01 | 11 | 0.965 | -0.314 | - | - | 0.26 | 0.01
12 | 0.991 | -0.173 | - | - | 0.25 | 0.11 | 12 | 0.971 | -0.18 | - | - | 0.25 | 0.11
13 | 0.992 | -0.11 | - | - | 0.2 | 0.1 | 13 | 0.972 | -0.115 | - | - | 0.2 | 0.1
14 | 0.982 | -0.37 | - | - | 0.89 | 0.83 | 14 | 0.962 | -0.386 | - | - | 0.89 | 0.83
15 | 0.978 | -1.629 | - | - | 2.5 | 1.2 | 15 | 0.958 | -1.697 | - | - | 2.5 | 1.2
16 | 0.983 | -0.671 | - | - | 0.09 | 0.04 | 16 | 0.963 | -0.756 | - | - | 0.09 | 0.04
17 | 0.978 | -1.042 | - | - | 0.26 | 0.03 | 17 | 0.958 | -1.142 | - | - | 0.26 | 0.03
18 | 0.962 | -1.799 | - | - | 0.59 | 0.2 | 18 | 0.942 | -1.932 | - | - | 0.59 | 0.2
19 | 0.944 | -2.39 | - | - | 0.93 | 0.43 | 19 | 0.923 | -2.549 | - | - | 0.93 | 0.43
20 | 0.982 | -0.565 | - | - | - | - | 20 | 0.963 | -0.645 | - | - | - | -
21 | 0.987 | 0.078 | - | - | -0.8 | -0.01 | 21 | 0.967 | 0.024 | - | - | -0.8 | -0.01
22 | 1 | 0.000* | 5.52 | 4.79 | - | - | 22 | 0.98 | 0 | 5.52 | 4 | - | -
23 | 1 | 3.135 | 1 | -0.94 | - | - | 23 | 1 | 1.223* | 0.96 | -0.18 | - | -
|  | Total: | 6.52 | 3.85 | 6.35 | 3.56 |  |  | Total: | 6.48 | 3.82 | 6.35 | 3.56
[8 empty] | Remarks: | Slack bus changed from bus 22 to bus 23
Too much of Pgen exceeding its rating out of generator at bus 22

## CaseWorstLoading
Case1 | No Q limits enforced | [5 empty] | Case2 | Q limits enforced
| Voltage Magnitude | Voltage Angle | [5 empty] | Voltage Magnitude | Voltage Angle
Bus |  |  | P_Gen | Q_Gen | P_Load | Q_Load | Bus |  |  | P_Gen | Q_Gen | P_Load | Q_Load
1 | 0.997 | 0.138 | - | - | - | - | 1 | 0.977 | 0.085 | - | - | - | -
2 | 0.976 | 0.258 | - | - | 1.19 | 0.61 | 2 | 0.966 | 0.043 | - | - | 1.19 | 0.61
3 | 0.996 | 0.114 | - | - | - | - | 3 | 0.976 | 0.061 | - | - | - | -
4 | 1 | -0.004 | - | - | - | - | 4 | 0.98 | -0.005 | - | - | - | -
5 | 0.984 | -0.599 | - | - | - | - | 5 | 0.964 | -0.683 | - | - | - | -
6 | 0.996 | 0.104 | - | - | - | - | 6 | 0.976 | 0.108 | - | - | - | -
7 | 1 | -0.004 | - | - | - | - | 7 | 0.98 | -0.005 | - | - | - | -
8 | 0.984 | -0.593 | - | - | - | - | 8 | 0.964 | -0.677 | - | - | - | -
9 | 0.983 | -0.59 | - | - | - | - | 9 | 0.963 | -0.674 | - | - | - | -
10 | 0.982 | -0.574 | - | - | - | - | 10 | 0.962 | -0.657 | - | - | - | -
11 | 0.984 | -0.279 | - | - | 0.28 | 0.01 | 11 | 0.964 | -0.35 | - | - | 0.28 | 0.01
12 | 0.991 | -0.173 | - | - | 0.25 | 0.11 | 12 | 0.97 | -0.181 | - | - | 0.25 | 0.11
13 | 0.991 | -0.124 | - | - | 0.21 | 0.1 | 13 | 0.971 | -0.13 | - | - | 0.21 | 0.1
14 | 0.981 | -0.447 | - | - | 1 | 0.85 | 14 | 0.961 | -0.467 | - | - | 1 | 0.85
15 | 0.978 | -1.629 | - | - | 2.5 | 1.2 | 15 | 0.957 | -1.699 | - | - | 2.5 | 1.2
16 | 0.983 | -0.68 | - | - | 0.09 | 0.04 | 16 | 0.962 | -0.768 | - | - | 0.09 | 0.04
17 | 0.978 | -1.051 | - | - | 0.26 | 0.03 | 17 | 0.957 | -1.155 | - | - | 0.26 | 0.03
18 | 0.962 | -1.808 | - | - | 0.59 | 0.2 | 18 | 0.941 | -1.946 | - | - | 0.59 | 0.2
19 | 0.943 | -2.425 | - | - | 0.94 | 0.43 | 19 | 0.922 | -2.592 | - | - | 0.94 | 0.43
20 | 0.982 | -0.574 | - | - | - | - | 20 | 0.962 | -0.657 | - | - | - | -
21 | 0.987 | 0.069 | - | - | -0.8 | -0.01 | 21 | 0.966 | 0.013 | - | - | -0.8 | -0.01
22 | 1 | 0.000* | 5.68 | 4.81 | - | - | 22 | 0.98 | 0 | 5.68 | 4 | - | -
23 | 1 | 3.131 | 1 | -0.94 | - | - | 23 | 1 | 1.160* | 0.96 | -0.16 | - | -
|  | Total: | 6.68 | 3.87 | 6.5 | 3.58 |  |  | Total: | 6.64 | 3.84 | 6.5 | 3.58
[8 empty] | Remarks: | Slack bus changed from bus 22 to bus 23
Too much of Pgen exceeding its rating out of generator at bus 22